## Slide 2
Service area – 36 sq mi
Total Population – 40,000
Bville Population – 37,000
Avg Daily WW – 6.5 MGD
WWM staff – 11
1 Vactor, 1 Rodder
1 Camera Van

## Slide 3
Golf Course
Lift Station
Hillcrest
Lift Station
Shawnee
Lift Station
Wastewater
Treatment Plant (7 mgd)
Woodland
Lift Station
Tuxedo
Lift Station
WASTEWATER SYSTEM MAP
LEGEND
Direction of flow per basin
Lift Station
Force Main
Treatment Plant
Limestone
Lift Station
To Ex. Flow Equalization Basin

## Slide 4
NO BYPASSES
Collection system:
270 miles
9,342 manholes

## Slide 5: BYPASS/OVERFLOW
AGING INFRASTRUCTURE
INFLOW/INFILTRATION
FOG
RAGS/WIPES
OTHER

## Slide 6
Collection system:
270 miles
9,342 manholes
NO BYPASSES
UP TO 2.5” RAIN EVENT

## Slide 7
Collection system:
270 miles
9,342 manholes
Year | Total # Bypasses
2014 | 21
2015 | 56
2016 | 36
2017 | 97
2018 | 11
2019 | 64
2020 | 72
2021 | 110
2022 | 24
2023* | 7
* Through end of Sept. | 
Year | Total # Bypasses | Bypasses caused by rain (I&I)
2014 | 21 | 33%
2015 | 56 | 77%
2016 | 36 | 75%
2017 | 97 | 80%
2018 | 11 | 0%
2019 | 64 | 72%
2020 | 72 | 69%
2021 | 110 | 74%
2022 | 24 | 71%
2023* | 7 | 0%
* Through end of Sept. |  | 
Year | Total # Bypasses | Bypasses caused by rain (I&I) | Rain events over 2.5 inches
2014 | 21 | 33% | 100%
2015 | 56 | 77% | 33%
2016 | 36 | 75% | 96%
2017 | 97 | 80% | 29% (58% -2.5 in evnts)
2018 | 11 | 0% | 0%
2019 | 64 | 72% | 74%
2020 | 72 | 69% | 34%
2021 | 110 | 74% | 62%
2022 | 24 | 71% | 47%
2023* | 7 | 0% | 0%
* Through end of Sept. |  |  | 
Year | Total # Bypasses | Bypasses caused by rain (I&I) | Rain events over 2.5 inches | Bypasses caused by grease, roots, or debris | Bypasses caused by disinfectant wipes | Bypasses caused by other (line breaks, pump failures, etc)
2014 | 21 | 33% | 100% | 52% | 0% | 14%
2015 | 56 | 77% | 33% | 20% | 0% | 4%
2016 | 36 | 75% | 96% | 22% | 0% | 3%
2017 | 97 | 80% | 29% (58% -2.5 in evnts) | 8% | 5% | 6%
2018 | 11 | 0% | 0% | 82% | 0% | 18%
2019 | 64 | 72% | 74% | 8% | 3% | 17%
2020 | 72 | 69% | 34% | 8% | 4% | 18%
2021 | 110 | 74% | 62% | 9% | 11% | 6%
2022 | 24 | 71% | 47% | 0% | 8% | 21%
2023* | 7 | 0% | 0% | 14% | 71% | 14%
* Through end of Sept. |  |  |  |  |  | 

## Slide 8
Collection system:
270 miles
9,342 manholes
Year | Total # Bypasses | Bypasses caused by rain (I&I) | Rain events over 2.5 inches
2014 | 21 | 33% | 100%
2015 | 56 | 77% | 33%
2016 | 36 | 75% | 96%
2017 | 97 | 80% | 29% (58% -2.5 in evnts)
2018 | 11 | 0% | 0%
2019 | 64 | 72% | 74%
2020 | 72 | 69% | 34%
2021 | 110 | 74% | 62%
2022 | 24 | 71% | 47%
2023* | 7 | 0% | 0%
* Through end of Sept. |  |  | 
Year | Total # Bypasses | Rainfall (in) | Rainfall (in) above/below Annual Avg. | Bypasses caused by rain (I&I) | Rain events over 2.5 inches | Bypasses caused by grease, roots, or debris | Bypasses caused by disinfectant wipes | Bypasses caused by other (line breaks, pump failures, etc)
2014 | 21 | 33.74 | -6.68 | 33% | 100% | 52% | 0% | 14%
2015 | 56 | 44.43 | 4.01 | 77% | 33% | 20% | 0% | 4%
2016 | 36 | 32.03 | -8.39 | 75% | 96% | 22% | 0% | 3%
2017 | 97 | 45.69 | 5.27 | 80% | 29% (58% -2.5 in evnts) | 8% | 5% | 6%
2018 | 11 | 34.03 | -6.39 | 0% | 0% | 82% | 0% | 18%
2019 | 64 | 55.18 | 14.76 | 72% | 74% | 8% | 3% | 17%
2020 | 72 | 40.8 | 0.38 | 69% | 34% | 8% | 4% | 18%
2021 | 110 | 39.44 | -0.98 | 74% | 62% | 9% | 11% | 6%
2022 | 24 | 28.28 | -12.14 | 71% | 47% | 0% | 8% | 21%
2023* | 7 | 20.49 | -19.93 | 0% | 0% | 14% | 71% | 14%
* Through end of Sept. |  |  |  |  |  |  |  | 

## Slide 9
Collection system:
270 miles
9,342 manholes
Year | Total # Bypasses | Footage Cleaned (ft) | SL-RAT (ft) | Point Repairs (ft) | Rainfall (in) | Rainfall (in) above/below Annual Avg. | Bypasses caused by rain (I&I) | Rain events over 2.5 inches
2014 | 21 | 646,433 | N/A | 411 | 33.74 | -6.68 | 33% | 100%
2015 | 56 | 645,688 | N/A | 1,205 | 44.43 | 4.01 | 77% | 33%
2016 | 36 | 649,200 | N/A | 1,921 | 32.03 | -8.39 | 75% | 96%
2017 | 97 | 1,101,179 | N/A | 1,726 | 45.69 | 5.27 | 80% | 29% (58% -2.5 in evnts)
2018 | 11 | 1,472,471 | N/A | 3,708 | 34.03 | -6.39 | 0% | 0%
2019 | 64 | 687,066 | N/A | 667 | 55.18 | 14.76 | 72% | 74%
2020 | 72 | 110,847 | 148,700 | 387 | 40.8 | 0.38 | 69% | 34%
2021 | 110 | 114,718 | 228,450 | 625 | 39.44 | -0.98 | 74% | 62%
2022 | 24 | 126,332 | 401,450 | 1,032 | 28.28 | -12.14 | 71% | 47%
2023* | 7 | 175,413 | 438,100 | 1,439 | 20.49 | -19.93 | 0% | 0%
* Through end of Sept. |  |  |  |  |  |  |  | 
Year | Total # Bypasses | Footage Cleaned (ft) | SL-RAT (ft) | Point Repairs (ft) | Rainfall (in) | Rainfall (in) above/below Annual Avg. | Bypasses caused by rain (I&I) | Rain events over 2.5 inches
2023* | 7 | 175,413 | 438,100 | 1,439 | 20.49 | -19.93 | 0% | 0%
2018 | 11 | 1,472,471 | N/A | 3,708 | 34.03 | -6.39 | 0% | 0%
2014 | 21 | 646,433 | N/A | 411 | 33.74 | -6.68 | 33% | 100%
2022 | 24 | 126,332 | 401,450 | 1,032 | 28.28 | -12.14 | 71% | 47%
2016 | 36 | 649,200 | N/A | 1,921 | 32.03 | -8.39 | 75% | 96%
2015 | 56 | 645,688 | N/A | 1,205 | 44.43 | 4.01 | 77% | 33%
2019 | 64 | 687,066 | N/A | 667 | 55.18 | 14.76 | 72% | 74%
2020 | 72 | 110,847 | 148,700 | 387 | 40.8 | 0.38 | 69% | 34%
2017 | 97 | 1,101,179 | N/A | 1,726 | 45.69 | 5.27 | 80% | 29% (58% -2.5 in evnts)
2021 | 110 | 114,718 | 228,450 | 625 | 39.44 | -0.98 | 74% | 62%
* Through end of Sept. |  |  |  |  |  |  |  | 

## Slide 10
Collection system:
270 miles
9,342 manholes
Year | Total # Bypasses | Footage Cleaned (ft) | SL-RAT (ft) | Point Repairs (ft) | Rainfall (in) | Rainfall (in) above/below Annual Avg. | Bypasses caused by rain (I&I) | Rain events over 2.5 inches
2014 | 21 | 646,433 | N/A | 411 | 33.74 | -6.68 | 33% | 100%
2015 | 56 | 645,688 | N/A | 1,205 | 44.43 | 4.01 | 77% | 33%
2016 | 36 | 649,200 | N/A | 1,921 | 32.03 | -8.39 | 75% | 96%
2017 | 97 | 1,101,179 | N/A | 1,726 | 45.69 | 5.27 | 80% | 29% (58% -2.5 in evnts)
2018 | 11 | 1,472,471 | N/A | 3,708 | 34.03 | -6.39 | 0% | 0%
2019 | 64 | 687,066 | N/A | 667 | 55.18 | 14.76 | 72% | 74%
2020 | 72 | 110,847 | 148,700 | 387 | 40.8 | 0.38 | 69% | 34%
2021 | 110 | 114,718 | 228,450 | 625 | 39.44 | -0.98 | 74% | 62%
2022 | 24 | 126,332 | 401,450 | 1,032 | 28.28 | -12.14 | 71% | 47%
2023* | 7 | 175,413 | 438,100 | 1,439 | 20.49 | -19.93 | 0% | 0%
* Through end of Sept. |  |  |  |  |  |  |  | 

## Slide 11
Collection system:
270 miles
9,342 manholes

## Slide 12: PILOT PROGRAM
Ex. Pump Stations can handle up to 4.5 times average flow
During rain events, peak flow was 18 times average flow
$750k TO UPGRADE PS AND FORCE MAIN
$1.75MM TO UPGRADE PS AND FORCE MAIN

## Slide 13: PILOT PROGRAM
95 CITY DEFECTS
73 MANHOLE FRAME SEALS
223 PRIVATE SIDE DEFECTS
134 UNCAPPED CLEANOUTS
89 SERVICE LINE DEFECTS
$300k – CITY DEFECTS
$250k – PRIVATE SIDE DEFECTS

## Slide 14
PILOT PROGRAM
PROPERTY OWNER SIGNS AGREEMENT:
  ALLOWS ACCESS FOR REPAIR
  INDEMNIFY THE CITY
  ACKNOWLEDGE SERVICE LINE REMAINS PROPERTY
  AND RESPONSIBILITY OF PROPERTY OWNER AFTER
  REPAIR IS COMPLETE
CITY HIRES A LICENSE PLUMBER TO PERFORM WORK
  PLUMBER PROVIDES A 1-YEAR WARRANTY TO
  PROPERTY OWNER
  ANY WARRANTY WORK BETWEEN PROPERTY
  AND PLUMBER

## Slide 15
PILOT PROGRAM
$20k ON CITY DEFECTS
$30k ON PRIVATE SIDE DEFECTS
99% COMPLETE
$10k ON CITY DEFECTS
$10k ON PRIVATE SIDE DEFECTS
5% COMPLETE

## Slide 16
Terry Lauritsen – (918) 338-4107; tllaurit@cityofbartlesville.org